## DB Configuration
RVJ RESIDENCE DB CONFIGURATION
Sr.No. | DB Specifications | Qty.
GROUND FLOOR
1 | GROUND FLOOR MAIN VTPN MCCB INCOMER DB
| 8-way VTPN MCCB Incomer DB | 1
INCOMER
| 125A, 4P, 25kA, MCCB | 1
OUTGOER'S
| 63A, 3P, MCB's | 5
| 40A, 3P, MCB's (Spare) | 2
| 32A, SP, MCB's (Spare) | 3
2 | UPS MAIN VTPN MCB INCOMER DB
| 6-way VTPN MCB Incomer DB | 1
INCOMER
| 63A, 4P, MCB | 1
OUTGOER'S
| 40A, 3P, MCB's | 2
| 32A, SP, MCB's | 3
| 20A, SP, MCB's | 9
3 | VISIBLE POWER MAIN'S TPN MCB INCOMER DB
| 6-way TPN MCB Incomer DB | 1
INCOMER
| 63A, 4P, MCB | 1
OUTGOER'S
| 20A, SP, MCB's | 18
4 | NON-VISIBLE POWER MAIN'S TPN MCB INCOMER DB
| 8-way TPN MCB Incomer DB | 1
INCOMER
| 63A, 4P, MCB | 1
OUTGOER'S
| 20A, SP, MCB's | 24
5 | AC INDOOR UNIT'S TPN MCB INCOMER DB
| 4-way TPN MCB Incomer DB | 1
INCOMER
| 40A, 4P, MCB | 1
OUTGOER'S
| 20A, SP, MCB's | 12
6 | LIGHTING & AUTOMATION (14 Module x 4 Stack DB) MCB INCOMER DB
| 14 Module x 4 Stack - MCB Incomer DB | 4
INCOMER
| 40A, 4P, MCB | 2
| 32A, DP, MCB | 2
OUTGOER'S
| 10A, SP, MCB's | 83
FIRST FLOOR
7 | FIRST MAIN VTPN MCCB INCOMER DB
| 8-way VTPN MCCB Incomer DB | 1
INCOMER
| 125A, 4P, 25kA, MCCB | 1
OUTGOER'S
| 63A, 3P, MCB's | 5
| 40A, 3P, MCB's (Spare) | 2
| 32A, SP, MCB's (Spare) | 3
8 | VISIBLE POWER MAIN'S TPN MCB INCOMER DB
| 6-way TPN MCB Incomer DB | 1
INCOMER
| 63A, 4P, MCB | 1
OUTGOER'S
| 20A, SP, MCB's | 18
9 | NON-VISIBLE POWER MAIN'S TPN MCB INCOMER DB
| 8-way TPN MCB Incomer DB | 1
INCOMER
| 63A, 4P, MCB | 1
OUTGOER'S
| 20A, SP, MCB's | 24
10 | AC INDOOR UNIT'S TPN MCB INCOMER DB
| 4-way TPN MCB Incomer DB | 1
INCOMER
| 40A, 4P, MCB | 1
OUTGOER'S
| 20A, SP, MCB's | 12
11 | LIGHTING & AUTOMATION (14 Module x 4 Stack DB) MCB INCOMER DB
| 14 Module x 4 Stack - MCB Incomer DB | 4
INCOMER
| 40A, 4P, MCB | 2
| 32A, DP, MCB | 2
OUTGOER'S
| 10A, SP, MCB's | 79
12 | FIRST FLOOR UPS TPN MCB INCOMER DB
| 4-way TPN MCB Incomer DB | 1
INCOMER
| 40A, 4P, MCB | 1
OUTGOER'S
| 32A, SP, MCB's | 3
| 20A, SP, MCB's | 9
SECOND FLOOR
13 | SECOND MAIN VTPN MCCB INCOMER DB
| 8-way VTPN MCCB Incomer DB | 1
INCOMER
| 125A, 4P, 25kA, MCCB | 1
OUTGOER'S
| 63A, 3P, MCB's | 5
| 40A, 3P, MCB's (Spare) | 2
| 32A, SP, MCB's (Spare) | 3
14 | VISIBLE POWER MAIN'S TPN MCB INCOMER DB
| 4-way TPN MCB Incomer DB | 1
INCOMER
| 63A, 4P, MCB | 1
OUTGOER'S
| 20A, SP, MCB's | 12
15 | NON-VISIBLE POWER MAIN'S TPN MCB INCOMER DB
| 8-way TPN MCB Incomer DB | 1
INCOMER
| 63A, 4P, MCB | 1
OUTGOER'S
| 20A, SP, MCB's | 24
16 | AC INDOOR UNIT'S TPN MCB INCOMER DB
| 4-way TPN MCB Incomer DB | 1
INCOMER
| 40A, 4P, MCB | 1
OUTGOER'S
| 20A, SP, MCB's | 12
17 | LIGHTING & AUTOMATION (14 Module x 4 Stack DB) MCB INCOMER DB
| 14 Module x 4 Stack - MCB Incomer DB | 4
INCOMER
| 40A, 4P, MCB | 2
| 32A, DP, MCB | 2
OUTGOER'S
| 10A, SP, MCB's | 71
18 | SECOND FLOOR UPS TPN MCB INCOMER DB
| 4-way TPN MCB Incomer DB | 1
INCOMER
| 40A, 4P, MCB | 1
OUTGOER'S
| 32A, SP, MCB's | 3
| 20A, SP, MCB's | 9
| List of Materials required for Sub-main Distribution | Qty
Distribution Borads
1 | 8-way VTPN MCCB Incomer DB's | 3
2 | 6-way VTPN MCB Incomer DB | 1
3 | 14module x 4 Stack MCB Incomer DB's | 12
4 | 8-way TPN MCB Incomer DB's | 3
5 | 6-way TPN MCB Incomer DB's | 2
6 | 4-way TPN MCB Incomer DB's | 6
SwitchGears
Incomers
6 | 125A, 4P, 25kA MCCB's | 3
7 | 63A, 4P, MCB's | 7
8 | 40A, 4P, MCB's | 11
9 | 32A, DP, MCB's | 6
Outgoers
10 | 63A, 3P, MCB's | 15
11 | 40A, 3P, MCB's | 8
12 | 32A, SP, MCB's | 18
13 | 20A,SP, MCB's | 183
15 | 10A, SP, MCB's | 233
Note on B46: Incomer Circuit Breakers need to confirmed from the Automation Vendor.
Note on B86: Incomer Circuit Breakers need to confirmed from the Automation Vendor.
Note on B134: Incomer Circuit Breakers need to confirmed from the Automation Vendor.

## GF Circuits RoomBook
RVJ RESIDENCE GROUND FLOOR LIGHTING, POWER & AC CIRCUITS ROOMBOOK
Sr. No | Area | 3R x 1.5 sqmm Cu. Fx. FRLS Circuits | 3R x 1.5 sqmm Cu. Fx. FRLS Circuits (Spare Circuits) | 3R x 2.5 sqmm Cu. Fx. FRLS Circuits (Non-Visible Power Outlets) | 3R x 2.5 sqmm Cu. Fx. FRLS Circuits (Visible Power Outlets) | 3R x 4.0 sqmm Cu. Fx. FRLS Circuits (AC Indoor Units)
1 | SitOut | 5 | 2 |  | 2 | 1
2 | Lounge | 5 | 2 |  | 2 | 2
3 | Dining & Staircase Lobby | 7 | 2 | 1 | 2
4 | Staircase | 4 |  | 1 | 1
5 | Parents Bedroom | 7 | 2 | 2 | 1
6 | Parents Bathroom | 6 |  | 2 | 1
7 | Wet Kitchen | 3 | 2 | 4 |  | 3
8 | Dry Kitchen | 5 | 2 | 3 | 3
9 | Formal Living | 6 | 2 |  | 1
10 | Lift Lobby | 3 |  |  | 1
11 | Foyer & Entrence | 5
12 | Deck | 6 | 1 |  | 2
13 | Water Body | 5 | 1
14 | 3R x 2.5 sqmm Cu. Fx. FRLS Circuits (Non-Visible Power Outlets for TV) |  |  | 3
| No.of Lighting Circuits | 67
| No.of Spare Lighting Circuits |  | 16
| Total No.of Lighting Circuits |  | 83
| Total No.of Non-Visible Power Outlets |  |  | 16
| Total No.of Visible Power Outlets |  |  |  | 16
| Total No.of AC Indoor Units |  |  |  |  | 6
Ground Floor DB Configuaration
|  |  |  | Main VTPN DB | 8-way VTPN MCCB Incomer DB | 1 No
| Ground Floor Circuit Details |  |  | UPS Main VTPN DB | 6-way VTPN MCB DB | 1 No
| Total No.of Lighting Circuits | 83 |  | Lighting & Automation | 14-Module 4-stack DB | 4 No's
| Total No.of Non-Visible Power Outlets | 16 |  | Non-Visible Power DB | 8-way TPN MCB DB | 1 No
| Total No.of Visible Power Outlets | 16 |  | Visible Power DB | 6-way TPN MCB DB | 1 No
| Total No.of AC Indoor Units | 6 |  | AC Indoor Units DB | 4-way TPN MCB DB | 1 No

## FF Circuits RoomBook
RVJ RESIDENCE FIRST FLOOR LIGHTING, POWER & AC CIRCUITS
Sr. No | Area | 3R x 1.5 sqmm Cu. Fx. FRLS Circuits | 3R x 1.5 sqmm Cu. Fx. FRLS Circuits (Spare Circuits) | 3R x 2.5 sqmm Cu. Fx. FRLS Circuits (Non-Visible Power Outlets) | 3R x 2.5 sqmm Cu. Fx. FRLS Circuits (Visible Power Outlets) | 3R x 4.0 sqmm Cu. Fx. FRLS Circuits (AC Indoor Units)
1 | Bedroom-2 | 7 | 2 | 3 | 1 | 2
2 | Bedroom-2 Bathroom | 7
3 | Bedroom-1 | 6 | 2 | 4 | 1 | 1
4 | Bedroom-1 Bathroom | 9
5 | Staircase Lobby | 3 |  |  | 2 | 2
6 | Master Bedroom | 5 | 2 | 2 | 1
7 | Master Bedroom WIC | 4 | 1 | 5
8 | Master Bathroom | 12 |  | 1 | 1
9 | FF Electrical room passage | 4 |  |  |  | 2
10 | Lounge Area | 6 | 3 | 1 | 2
11 | Open to Sky Area(Courtyard) | 2 | 4
15 | 3R x 2.5 sqmm Cu. Fx. FRLS Circuits (Non-Visible Power Outlets for TV) |  |  | 3
| No.of Lighting Circuits | 65
| No.of Spare Lighting Circuits |  | 14
| Total No.of Lighting Circuits |  | 79
| Total No.of Non-Visible Power Outlets |  |  | 19
| Total No.of Visible Power Outlets |  |  |  | 8
| Total No.of AC Indoor Units |  |  |  |  | 7
First Floor DB Configuaration
| First Floor Circuit Details |  |  | Main VTPN DB | 8-way VTPN MCCB Incomer DB | 1 No
| Total No.of Lighting Circuits | 79 |  | Lighting & Automation | 14-Module 4-stack DB | 4 No's
| Total No.of Non-Visible Power Outlets | 19 |  | Non-Visible Power DB | 8-way TPN MCB DB | 1 No
| Total No.of Visible Power Outlets | 8 |  | Visible Power DB | 6-way TPN MCB DB | 1 No
| Total No.of AC Indoor Units | 7 |  | AC Indoor Units DB | 4-way TPN MCB DB | 1 No
|  |  |  | UPS DB | 4-way TPN MCB DB | 1 No

## SF Circuits RoomBook
RVJ RESIDENCE SECOND FLOOR LIGHTING, POWER & AC CIRCUITS ROOMBOOK
Sr. No | Area | 3R x 1.5 sqmm Cu. Fx. FRLS Circuits | 3R x 1.5 sqmm Cu. Fx. FRLS Circuits (Spare Circuits) | 3R x 2.5 sqmm Cu. Fx. FRLS Circuits (Non-Visible Power Outlets) | 3R x 2.5 sqmm Cu. Fx. FRLS Circuits (Visible Power Outlets) | 3R x 4.0 sqmm Cu. Fx. FRLS Circuits (AC Indoor Units)
1 | Gym | 3 | 2 | 2 |  | 1
2 | SitOut | 5 | 2 |  | 1
3 | SPA room | 5 | 2 | 1 | 2
4 | Lift Behind Electrical room | 5 | 2 | 2 |  | 2
5 | Yoga room | 5 | 2 | 2 |  | 1
6 | Home Theatre | 9 | 3 | 3 |  | 2
7 | Lift Lobby | 2 | 1
8 | Staircase Lobby | 2 | 3 |  | 1
9 | Bedroom | 5 | 3 | 4 | 1 | 1
10 | BR Bathroom | 9 | 1 | 1 | 1
14 | 3R x 4.0 sqmm Cu. Fx. FRLS Circuits (WC Power Outlets) |  |  | 3
| No.of Lighting Circuits | 50
| No.of Spare Lighting Circuits |  | 21
| Total No.of Lighting Circuits |  | 71
| Total No.of Non-Visible Power Outlets |  |  | 18
| Total No.of Visible Power Outlets |  |  |  | 6
| Total No.of AC Indoor Units |  |  |  |  | 7
Second Floor DB Configuaration
| Second Floor Circuit Details |  |  | Main VTPN DB | 8-way VTPN MCCB Incomer DB | 1 No
| Total No.of Lighting Circuits | 71 |  | Lighting & Automation | 14-Module 4-stack DB | 4 No's
| Total No.of Non-Visible Power Outlets | 18 |  | Non-Visible Power DB | 8-way TPN MCB DB | 1 No
| Total No.of Visible Power Outlets | 6 |  | Visible Power DB | 4-way TPN MCB DB | 1 No
| Total No.of AC Indoor Units | 7 |  | AC Indoor Units DB | 4-way TPN MCB DB | 1 No
|  |  |  | UPS DB | 4-way TPN MCB DB | 1 No